11/24/2014

SUGGESTED SPECIFICATIONS

TAMCO SERIES 1000 SM SW, UL/ULC APPROVED SMOKE DAMPER

WITH SALT WATER RESISTANCE OPTION

- Extruded aluminum (6063-T5) damper frame shall not be less than 0.080” (2.03 mm) in thickness. Damper frame shall be 4” (101.6 mm) deep x 1" (25.4 mm), with duct mounting flanges on both sides of frame. Damper frame shall have a 2" (50.8 mm) mounting flange on the rear of the damper when installed as Extended Rear Flange install type. Aluminum frame shall be clear anodized to a minimum thickness of 0.7 mil (18 microns) deep. Frame shall be assembled using stainless steel screws. Welded frames shall not be acceptable.

- Blades shall be maximum 6.4” (162.6 mm) deep extruded aluminum (6063-T5) air-foil profiles with a minimum wall thickness of 0.06” (1.52mm), clear anodized to a minimum thickness of 0.7 mil (18 microns) deep.

- Blade seals shall be specially designed and engineered extruded silicone, secured in an integral slot within the aluminum blade extrusions and shall be mechanically fastened to prevent shrinkage and movement over the life of the damper. Adhesive or clip-on type blade seals will not be approved.

- Frame seals shall be specially designed and engineered extruded silicone, secured in an integral slot within the aluminum frame extrusions and shall be mechanically fastened to prevent shrinkage and movement over the life of the damper. Metallic compression type jamb seals will not be approved.

- Bearings shall be a dual bearing system composed of a bronze oilite inner bearing (fixed around a 7/16" (11.11 mm) aluminum hexagon blade pivot pin), rotating within a bronze oilite outer bearing inserted in the frame. Single axle bearing, rotating in an extruded or punched hole shall not be acceptable.

- Hexagonal control shaft shall be 7/16" (11.11 mm). It shall have an adjustable length and shall be an integral part of the blade axle. A field-applied control shaft shall not be acceptable. All parts shall be stainless steel.

- Linkage hardware shall be aluminum and stainless steel, installed in the frame side, out of the airstream, and accessible after installation. Linkage hardware shall be complete with cup-point trunnion screws to prevent linkage slippage. Trunnion bearings shall be bronze oilite. Linkage that consists of steel rubbing steel will not be approved.

- Smoke dampers are to be designed for operation in temperatures ranging between -40°F (-40°C) and 250°F (121°C).

- Smoke dampers shall be UL/ULC rated Leakage Class 1.

- Smoke dampers shall be AMCA certified for Air Performance under the AMCA Certified Ratings Program.

- Smoke dampers shall be parallel blade action.

- Smoke dampers shall be custom made to required size, with blade stops not exceeding 1¼” (31.7 mm) in height.

- Smoke dampers shall be installed in the following manner:  Flanged to Duct, Installed in Duct, or Extended Rear Flange. (Specify one.)

- Actuators shall be factory-mounted as required by UL 555S/ULC-S112.1.

- Approved actuators shall be Belimo - Voltage: 24, 120 or 230 vac, single phase. (Specify one voltage.)

- Actuator mounting location shall be Internal or External. (Specify one.) All smoke dampers with internally mounted actuators shall be mounted on a jack shaft.

- Auxiliary switches shall be available as an actuator option.

- Installation of dampers must be in accordance with TAMCO’s current UL/ULC Approved Smoke Damper Installation Guidelines, provided with each damper shipment.

- Acceptable product shall be TAMCO Series 1000 SM SW, UL/ULC Approved Smoke Damper with Salt Water Resistance Option, as manufactured by T. A. Morrison & Co., Inc. (Tel: 1-800-561-3449, USA & Canada)