11/24/2014

SUGGESTED SPECIFICATIONS

TAMCO SERIES 3000 INTAKE LOUVERS 	TAMCO SERIES 4000 EXHAUST LOUVERS

SERIES 3200 (2” deep blade)	SERIES 4200 (2” deep blade)

SERIES 3400 (4” deep blade)	SERIES 4400 (4” deep blade)

SERIES 3600 (6” deep blade)	SERIES 4600 (6” deep blade)

- Louver frames shall be extruded mill finish aluminum (6063-T5). (Specify one louver depth and frame extrusion thickness.)

  - Louvers with 2” (50.8 mm) and 4” (101.6mm) frames shall not be less than 0.072" (1.83mm) in thickness.

  - Louvers with 6” (152.4 mm) frames shall not be less than 0.098" (2.50mm) in thickness.

- Louvers frame style shall be Channel (U-frame) type or Exterior Flange (L-frame) style. (Specify one.)

- Louver blades shall be extruded mill finish aluminum (6063-T5) and shall be fixed at a 45° angle. Intake louvers shall have a center baffle (K type) blade to resist water intake. Exhaust louvers shall have a flat (J type) blade for lower pressure drop.

  - 2” (50.8 mm) blade profiles shall not be less than .063" (1.60mm) in thickness.

  - 4” (101.6mm) blade profiles and shall not be less than .071" (1.80mm) in thickness.

  - 6” (152.4 mm) blade profiles and shall not be less than .081" (2.06mm) in thickness.

- Louvers shall be mullion style or continuous blade style, as indicated on the plans.

- Screens to be constructed as follows: (Specify one.)

- Standard bird screen shall be .5" x .5" x .032” (12.7mm x 12.7mm x .81mm) galvanized steel wire mesh, complete with frame and installed by the manufacturer.

- Stainless steel bird screen shall be constructed of .5" x .5" x .063” (12.7mm x 12.7mm x 1.60mm) stainless steel wire mesh and shall be installed by the manufacturer.

- Aluminum bird screen shall be constructed of .59" x 1.20" x .045” (15mm x 30.5mm x 1.14mm) inter-crimped aluminum wire mesh and shall be installed by the manufacturer.

- Insect screen shall be constructed of 18 x16/in.² (7.1x 6.3/cm²) aluminum mesh. The gauge shall be .012" (0.30mm).  Insect screen shall be installed by the manufacturer.

- Louvers shall be made to size required.

- Acceptable product shall be TAMCO Series 3200, 3400, 3600 / 4200, 4400, 4600 fixed blade louvers as supplied by T. A. Morrison & Co., Inc. (Tel: 1-800-561-3449, USA & Canada)