11/24/2014

SUGGESTED SPECIFICATIONS

TAMCO SERIES 7000 WT WEIGHTED BACK DRAFT DAMPER

- Extruded aluminum (6063-T5) back draft damper frame shall not be less than 0.060” (1.52 mm) in thickness.  Weighted back draft damper frame shall be 2.5” (63.5 mm) deep. Frame to be assembled using zinc-plated steel mounting fasteners. Welded frames shall not be acceptable.

- Blades shall be maximum 5” (127 mm) deep extruded aluminum (6063-T5) profiles and shall not be less than .060" (1.52 mm) in thickness.

- Each blade shall be manufactured with a mounting hole to receive a front-mounted mechanical weight.  Weights shall be supplied, so that the required resistance to the opening of the blade against air flow can be increased.

- Blade seals shall be extruded silicone, secured in an integral slot within the aluminum blade extrusions and shall be mechanically fastened to prevent shrinkage and movement over the life of the damper. Adhesive or clip-on type blade seals will not be approved.

- Frame seals shall be extruded silicone, secured in an integral slot within the aluminum frame extrusions and shall be mechanically fastened to prevent shrinkage and movement over the life of the damper. Frames without seals will not be approved.

- Maintenance-free bearings system shall be composed of a ½" (12.7 mm) aluminum pivot point rotating in a Celcon bearing.

- Linkage system shall consist of hard alloy aluminum (6005-T6) crank arms fastened to aluminum pivot rods and shall be secured within a channel running along top of blades. Large diameter 11/32" (8.73 mm) hard alloy aluminum (6065-T6C) linkage rod shall connect the crank arms by means of a zinc-plated steel trunnion. Linkage that consists of metal rubbing metal will not be approved.

- Trunnions shall be zinc-plated to provide a hard, smooth and long-lasting rotating surface for the bearing and shall be secured to the linkage by cup-point screws to prevent linkage slippage.

- Weighted back draft dampers shall be designed for operation in temperatures ranging between -40°F (-40°C) and 212°F (100°C).

- Air leakage through a 24" x 24" (610 mm x 610 mm) back draft damper shall not exceed 4.32 cfm/ft² (21.95 l/s/m²) against 1" w.g. (0.25 kPa) differential static pressure at standard air.

- Weighted back draft dampers shall be custom made to required size. Minimum section size shall be 6" wide x 6" high (153 mm x 153 mm). Maximum section size shall be 36” wide x 48.625” high (915 mm x 1235 mm).

- Weighted back draft dampers with dimensions greater than maximum section size shall be manufactured in multiple sections. Multiple sections are not interlinked or connected. To install, each section must be individually fastened to a structural frame prepared on site.

- Weighted back draft dampers shall be installed in the following manner: Rear Flange, In Duct, or Front Flange. (Specify one.)

- Acceptable product shall be TAMCO Series 7000 WT Weighted Back Draft Damper, as manufactured by
 T. A. Morrison & Co., Inc. (Tel: 1-800-561-3449, USA & Canada)