[image: image1.png]



Energy (Btu) Measurement System Specification

For High Temp Heating Applications (280 to 440 deg. F)
  
AUG 2013
Energy Measurement System Specification 

The entire Energy Measurement System shall be provided by a single manufacturer, ONICON Incorporated, and shall consist of a flow meter, two temperature sensors, a Btu meter, temperature thermowells, and all required mechanical installation hardware. A certificate of calibration shall be provided with each system. 

Btu Meter:  Provide an ONICON System-10 BTU Meter. The Btu meter shall provide the following points both at the integral LCD and as outputs to the building control system: Energy Total, Energy Rate, Flow Rate, Supply Temperature and Return Temperature. Output points shall be transmitted via serial network (protocol conforming to BACnet MS/TP, BACnet/IP, LONWORKS®, JCI-N2, MODBUS RTU RS485, MODBUS RTU TCP/IP or Siemens-P1) with optional individual analog and pulse outputs available.  Each Btu meter shall be factory programmed for its specific application, and shall be re-programmable using the front panel keypad (no special interface device or computer required). 
Temperature sensors: Temperature sensors shall be industrial grade 100 ohm platinum RTDs with matched 4-20 mA transmitters and 316L SS thermowells configured for high temperature applications.  Temperature sensors shall be bath-calibrated and matched (NIST* traceable) for the specific temperature range for each application. The calculated differential temperature used in the energy calculation shall be accurate to within +0.15°F (including the error from individual temperature sensors, sensor matching, input offsets, and calculations).  
Flow Meter:  Furnish and install an ONICON Model F-4200 Clamp-on Transit Time Ultrasonic Flow Meter, complete with matched high temperature transducers, self-aligning installation hardware and coaxial transducer cables. The flow meter shall be installed without making any openings in the pipe wall and shall utilize non-wetted ultrasonic transducers that may be located up to 300 ft from the meter. Ultrasonic transducers provided must be optimized for the specific pipe & process conditions for each application and the transducer frequency shall be automatically matched to the resonant frequency of the pipe at start-up. An integral auto-zero function shall be provided for zero precision and high accuracy, even at very low flow velocities. The flow meter shall be capable of measuring bi-directional flow. Accuracy shall be within ± 1% of rate from 1 to 40 ft/sec and ± 0.01 ft/sec for velocities below 1 ft/sec. Overall turndown shall exceed 400:1The meter shall display flow rate and flow total with an integral LCD display and support field programming of all parameters.  The meter shall also have integral diagnostics to verify installation conditions and the proper operation of the meter.  The meter shall provide a loop-powered 4-20 mA output signal for connection to the System-10 Btu Meter.  In addition, an integral pulse output for flow totalization shall be provided.  All outputs shall be linear with flow rate. 

.  

* U.S. National Institute of Standards and Technology
11451 Belcher Road South, Largo, FL 33773 • USA • Tel +1 (727) 447-6140 • Fax (727) 442-5699       www.onicon.com • sales@onicon.com


