[image: image1.png]



Flow Measurement Specification

F-5100 Insertion Thermal Mass Flow Meter
For Combustible Gas Applications
                  

                        AUG 2013 

Flow Meter Specification 

Provide an ONICON Model F-5100 Insertion Thermal Mass Flow Meter, complete with all installation hardware necessary to enable insertion and removal of the meter without system shutdown. The flow meter shall be hand-insertable up to 250 psi. Provide a flow conditioner if required to meet the manufacturer’s minimum upstream straight pipe run requirement. For pipe sizes smaller than 1½” provide an ONICON Model F-5100 Inline Thermal Mass Flow Meter. Materials of construction for wetted metal components shall be 316 SS.  The flow meter shall provide SFPM* flow readings from a pair of encapsulated platinum sensors and shall not require additional temperature or pressure compensation. In addition, the meter shall continuously display information that can be used to validate the calibration of the meter.   Each flow meter shall be individually wet-calibrated against a standard that is directly traceable to NIST**.  A certificate of calibration shall be provided with each flow meter. Accuracy shall be within ± 1% of rate from 500-7000 SFPM and ± 2% of rate from 100-500 SFPM. Overall turndown shall exceed 1000:1.  Output signals shall consist of the following: (1) analog 4-20mA output and (1) scalable pulse output for totalization.  The meter shall be equipped with an integrally mounted graphical display that may be optionally remote mounted up to 1000 ft from the sensor. Each flow meter shall be covered by the manufacturer’s two-year warranty. 

Optional Flow Display: Provide a D-100 Series Display Module for local or remote indication of flow rate and total. Output signals shall be either serial network (protocol conforming to BACnet® MS/TP, BACnet/IP, LONWORKS®, MODBUS RTU RS485, MODBUS RTU TCP/IP, JCI-N2, or Siemens-P1) or via individual analog and pulse outputs.

*Standard Feet per Minute
** National Institute of Standards and Technology

11451 Belcher Road South, Largo, FL 33773 • USA • Tel +1 (727) 447-6140 • Fax (727) 442-5699       www.onicon.com • sales@onicon.com

