EBTRON SPECIFICATION FOR FAN INLET FLOW MEASUREMENT:

PART 2
PRODUCTS

2.1
PRODUCTS INCLUDED IN THIS SECTION

A.
Fan inlet mounted airflow and temperature measurement devices

2.2
ACCEPTABLE MANUFACTURERS
A.
Subject to compliance with performance and design requirements of this Section, provide products that comply with this specification by one of the following vendors:

1.
EBTRON, Inc. Model HTx104-F (basis of design) 

a)
Alternatives requesting acceptance as “equals” less than 30 days prior to bid date or products submitted in non-conformance with the requirements of this specification will not be considered. 

b)
For any product to be considered for substitution a written section-by-section detailed exceptions/compliance document shall be submitted to the Engineer before any approval will be considered.

c)
Any firm submitting a product as an equal shall make available a functioning non-fan powered demonstration sample for review in the specifying engineer’s office.  

B.
Upon submission, the following alternates will be acceptable, if configured to meet all of the performance requirements and functions detailed within this specification: 

1.   Kurz Instruments

2.   Sierra Instruments

3.   FCI
C.
Specific technologies listed below are excluded. 
1.
Vortex shedding devices are not acceptable. 

2.
Pitot tubes, arrays, Piezo rings and other differential pressure based devices are not acceptable. 

2.3
AIRFLOW/TEMPERATURE MEASUREMENT DEVICES (ATMD)
A. 
Provide airflow/temperature measurement devices (ATMDs) where indicated on the plans.  
B.
Each ATMD shall consist of one or more sensor probes and a single, remotely mounted, microprocessor-based transmitter capable of independently processing up to 4 independently wired sensor nodes contained in one or more probe assemblies per measurement location.  
1.
Each sensor node shall contain two individually wired, hermetically sealed bead-in-glass thermistors.  
2.
Thermistors shall be mounted in the sensor node using a marine-grade, waterproof epoxy.  Thermistor leads shall be protected and not exposed to the environment.  Thermistor leads shall not be fastened to the thermistor semiconductor substrate by weld or solder connections.
3.
The airflow rate at each sensor node shall be equally weighted and arithmetically averaged by the transmitter prior to output.  All integrated circuitry shall be temperature rated as ‘industrial-grade’.  Submissions containing ‘commercial-grade’ integrated circuitry are not acceptable.
4.
The temperature at each sensor node shall be equally weighted arithmetically averaged or velocity weighted and averaged by the transmitter prior to output, field-selectable by the contractor or user.  
5.
Each transmitter shall have a 16-character alpha-numeric display capable of displaying airflow, temperature, system status, configuration settings and diagnostics.  
6.
Other than the thermistor sensors, no other electronic components shall be located at the sensing node.

7.
Devices using chip-in-glass, epoxy-coated or diode-case chip thermistors are not acceptable.   

8.
Devices with RJ-45 connections exposed to the environment or having electronic circuitry mounted in or at the sensor node are not acceptable.  
C.
Fan Inlet Sensor Probes Design and Performance
1.
Each sensor node, consisting of two thermistor-sensors and their structural housing, shall independently determine the airflow rate and temperature at each measurement point.
2.
Each sensor node shall be factory calibrated at a minimum of 16 airflow rates and 3 temperatures to standards that are traceable to the National Institute of Standards and Technology (NIST).  Thermistor sensor calibrations traceable only to temperature standards are not acceptable. 
3.
Airflow accuracy shall be ± 2% of Reading over the entire operating airflow range of not less than 0 to 10,000 fpm (50.8 m/s).
a)
Devices whose overall performance at the host controller input terminals is the combined accuracy of the transmitter and sensor probes shall demonstrate that the total accuracy meets the performance requirements of this specification throughout the measurement range.

4.
Temperature accuracy shall be ± 0.14°F (0.08°C) over the entire operating temperature range of -20°F to 160°F (-28.9°C to 71°C).
5.
The operating humidity range for each sensor probe shall be 0-99% RH (non-condensing).  Product design shall consider direct exposure to or emersion in liquid water and temporary exposure shall not damage the sensing elements.
6.
Each sensor or probe assembly shall not require matching to the transmitter in the field.

7.
A single manufacturer shall provide both the airflow/temperature measuring probe(s) and transmitter for each measurement location.

8.
Sensor node assemblies shall be mounted on Type 304 stainless steel housings.  

9.
Mounting rods shall be field adjustable to fit the fan inlet and constructed of zinc plated steel.  

10.
Mounting feet shall be constructed of Type 304 stainless steel. 

11.
Mounting styles required shall be indicated on the plans as either “face mount,” “forward mount” or “throat mount.”  

i.
Face and Forward mounting styles shall provide no mechanical fastening in the throat of the inlet cone and shall be used on all inlet condition-sensitive plenum-type or plug fans.
12.
Fan inlet probe cables shall be UL plenum-rated and may be FEP or PVC jacketed.
D.
Transmitters

1.
The transmitter shall have an integral, minimum 16-character LCD display capable of simultaneously displaying airflow and temperature. The LCD display shall also be capable of displaying individual airflow and temperature readings of each independent sensor node.
2.
The transmitter shall be capable of field configuration, diagnostics and include Field Calibration software, all using an on-board pushbutton interface and the LCD display.  Field Calibration Wizard shall allow for a one or two point field adjustment to factory calibration for installations that require adjustment.
3.
The transmitter shall have an on-off power switch and operate on 24 VAC.  Isolation transformers shall not be required.  
a)
The transmitter shall use a 24 VAC power supply, fused and protected from over voltage, over current and power surges.  
b)
The transmitter shall use “watch-dog” circuitry to assure automatic reset after power disruption, transients and brown-outs.
4.
The operating temperature range for the transmitter shall be -20° F to 120° F (-28.9° C to 48.9° C).  The transmitter shall be installed at a location that is protected from weather and water.

5.
The transmitter shall be capable of communicating with other devices using one of the following interface options:

a)
Linear analog output signals for airflow and temperature: Field selectable, fuse protected, galvanically and optically isolated from all other circuitry, as either 0-5 VDC, 0-10 VDC or 4-20 mA (all 4-wire connections).  
i.
Analog outputs shall have a minimum resolution 0.025% F.S.  
ii.
An alarm output shall be available with the analog output option, adjustable to provide either a minimum or maximum signal when airflow is outside of a preset acceptable operating range.  The alarm output shall provide adjustable hysteresis.
b)
RS-485: Field selectable BACnet-MS/TP or Modbus-RTU network protocols. 
6.
The transmitter shall be capable of identifying a ‘damaged’ sensor node and continue to operate by correctly averaging the remaining sensor nodes.
E.
The manufacturer’s authorized representative shall review and approve placement and operating airflow rates for each measurement location indicated on the plans.  
1.
A written report shall be submitted to the consulting mechanical engineer if any measurement locations do not meet the manufacturer’s placement requirements.


F.  Ebtron manufacture representative: Bluefield Engineered Systems, 888 445-HVAC (4822)


- 1

